## Sheet1
Object ID | Signal name | String ID | En Reg | En Addr | En TPConfigDW | En condition | en bit pos | reg | addr | State L1 | State L2 | State L3 | State L4 | State L5 | State L6 | State L7 | State L8 | State L9
#GROUP# MAIN DIGITAL
0x2202 'Unit1\PlantPoint' | Operating mode | 1 | 1 | 701 |  |  |  | 4 | 21 | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling
0x2202 'Unit1\PlantPoint' | Act Operating mode | 2 | 1 | 701 |  |  |  | 3 | 121 | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling
0x2302 'Unit1\TempControl.TmpRegSel' | Tmp control mode | 3 | 0 | 843 |  |  |  | 4 | 22 | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT
0x2302 'Unit1\aoHumitityControl.HumRegSel' | Hum control mode | 4 | 1 | 850 |  |  |  | 4 | 24 | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH
0x2202 'Unit1\aoHumitityControl.SPSELHumidity' | Hum stpt selection | 5 | 1 | 850 |  |  |  | 4 | 25 | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz
0x2302 'Unit1\FanControl.ExtFan2OpMode' | 2 Extract fan mode | 6 | 4 | 811 |  | > 0 |  | 4 | 29 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan3OpMode' | 3 Extract fan mode | 7 | 4 | 812 |  | > 1 |  | 4 | 30 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan4OpMode' | 4 Extract fan mode | 8 | 4 | 813 |  | > 2 |  | 4 | 31 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan5OpMode' | 5 Extract fan mode | 9 | 4 | 814 |  | > 3 |  | 4 | 32 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan6OpMode' | 6 Extract fan mode | 10 | 4 | 815 |  | > 4 |  | 4 | 33 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan7OpMode' | 7 Extract fan mode | 11 | 4 | 816 |  | > 5 |  | 4 | 34 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan8OpMode' | 8 Extract fan mode | 12 | 4 | 817 |  | > 6 |  | 4 | 35 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan9OpMode' | 9 Extract fan mode | 13 | 4 | 818 |  | > 7 |  | 4 | 36 | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.DmpDlyOffFireEn' | Damper dly off - fire | 14 |  |  | 0 |  | 4 | 0 | 35 | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 'Unit1\FanControl.FireMode' | Fire mode | 15 |  |  | 0 |  | 6 | 4 | 26 | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn
#GROUP# ADVANCED DIGITAL
0x2302 'InOutp\InOutp.SFDiffPSenScale' | Scale pressure supply fan | 1
0x2302 'InOutp\InOutp.EFDiffPSenScale' | Scale pressure extract fan | 2
0x2302 'Unit1\ModbusMS.MB_FanErrEn' | Modbus fan error | 3
0x2302 'Unit1\TempControl.CasCtrEn' | Cascade controller | 4
0x2302 'Unit1\TempControl.DehumSpvMinTEn' | Dehum tmp min stpt | 5
0x2302 'Unit1\TempControl.TOutThEn' | Disable by outs tmp | 6
0x2302 0x00003AB1 | El heating | 7
0x2302 'Unit1\FanControl.AirQRegSel' | Air quality control | 8
0x2302 'Unit1\FanControl.AirQAveMinMax' | Air quality mix | 9
0x2302 'Alarms\Alarms.ComAlarmPol' | Common alarm polarity | 10
0x2302 0x0000DD29 | Enable all obj. | 11
0x2302 0x0000371C | Auto configuration IOs | 12
0x2302 0x0000236A | Room unit | 13
0x2302 0x00006C01 | Tmp stpt selection | 14
0x2203 'Unit1\AnalogInp.HuRelRoom' | Humidity | 15
0x2302 0x00007DD0 | Dehumidification | 16
0x2302 0x00009B65 | Common alarm | 17
#GROUP# ADVANCED INPUTS
0x2302 0x00008D0B | Outs air dampr fdbk | 1
0x2302 0x00006BC8 | Exh air dampr fdbk | 2
0x2302 0x0000558F | Extract air pressure | 3
0x2302 0x00008D92 | Supply air pressure | 4
0x2302 0x00001E6B | Supply air pressure switch | 5
0x2302 0x0000322C | Extract air pressure switch | 6
0x2302 0x0000ADAC | Air flow switch | 7
0x2302 0x00007009 | Filter alarm | 8
0x2302 0x00001F3D | Fresh air filter | 9
0x2302 0x0000E4D0 | Supply filter | 10
0x2302 0x000081DE | Extract filter | 11
0x2302 0x0000E4CE | Exhaust filter | 12
0x2302 0x000025E3 | 2 Aux supply filter | 13
0x2302 0x00009D2B | 3 Aux supply filter | 14
0x2302 0x0000D725 | 2 Aux extract filter | 15
0x2302 0x00009476 | 3 Aux extract filter | 16
0x2302 0x0000845F | Remote start | 17
0x2302 0x0000938D | Air quality | 18
0x2302 0x00003938 | Outdoor temperature | 19
0x2302 0x000080F9 | Outside air temp | 20
0x2302 0x00009C60 | Supply air temp | 21
0x2302 0x0000B835 | Extract air temp | 22
0x2302 0x0000ABE4 | Room tmp sensor | 23
0x2302 0x0000D78F | Tmp before cooler | 24
0x2302 0x00000F0D | Tmp after cooler | 25
0x2302 0x00008CD4 | B11-Temperature | 26
0x2302 0x0000D584 | B12-Temperature | 27
0x2302 0x0000AF39 | Aux tmp sensor | 28
0x2302 0x000001CC | Humidifier | 29
0x2302 0x0000F9BC | Outs air hum rel | 30
0x2302 0x000082CA | Extract air hum rel | 31
0x2302 0x0000C4B4 | Room humidity rel | 32
0x2302 0x0000B9D0 | Cooling pump | 33
0x2302 0x00004517 | Compressor | 34
0x2302 0x00000ECF | Fire damper closed | 35
0x2302 0x00004AB6 | External setpoint | 36
#GROUP# ADVANCED FAN
0x2302 0x00003D9C | Fan control mode | 1
0x2302 0x0000236A | Room unit | 2
0x2302 0x0000E408 | Duct pres stpt by rm unit | 3
0x2302 0x00006048 | Following system | 4
0x2302 0x0000F474 | Fans nr | 5
0x2302 0x000064CF | Outputs fans | 6
0x2302 0x00001010 | Fan state | 7
0x2302 0x00009AB1 | Dampers | 8
0x2302 0x0000952F | Supply fan | 9
0x2302 0x0000F838 | Extract fan | 10
0x2302 0x00005CFB | 2 Extract fan | 11
0x2302 0x00006BCB | 3 Extract fan | 12
0x2302 0x0000EE5B | 4 Extract fan | 13
0x2302 0x0000D96B | 5 Extract fan | 14
0x2302 0x0000803B | 6 Extract fan | 15
0x2302 0x0000B70B | 7 Extract fan | 16
0x2302 0x00009B3A | 8 Extract fan | 17
0x2302 0x0000AC0A | 9 Extract fan | 18
0x2302 0x00000A27 | Supply VAVs | 19
0x2302 0x00000ECF | Fire damper closed | 20
#GROUP# ADVANCED TEMP
0x2302 0x00006C01 | Tmp stpt selection | 1
0x2302 0x0000C8DA | Chovr type select | 2
0x2302 0x00002CF9 | Hrec frost protect | 3
0x2302 0x00007924 | Pre heating | 4
0x2302 0x0000C2F3 | Free cooling | 5
0x2302 0x000048AB | Mixing damper | 6
0x2302 0x000029A3 | Heat recovery | 7
0x2302 0x0000C73F | Heating | 8
0x2302 0x000077B6 | Cooling | 9
0x2302 'Unit1\TempControl.ElHeaterInSeq' | El heating | 10
0x2302 0x000061F0 | El heater on ext | 11
0x2302 0x00007400 | 2 El heating | 12
0x2302 0x000034FF | 3 El heating | 13
0x2302 0x000010EB | VRF type sel | 14
0x2302 0x000049F1 | VRF in sequence | 15
0x2302 0x0000C130 | VRF reg by dT | 16
0x2302 0x0000CD70 | VRF vent mode | 17
0x2302 0x0000C67E | VRF auto mode | 18
0x2302 0x00005182 | VRF 2 | 19
0x2302 0x00003817 | Siphon heater | 20
0x2302 0x0000A45A | Piping heater | 21
Note on A42: Author: Ispitiati točku