## Sheet1
Version: 1
Var name | Value | State Lan1 | State Lan2 | State Lan3 | State Lan4 | State Lan5 | State Lan6 | State Lan7 | State Lan8 | State Lan9
FIRE_DAMPR_EN_REG | 4
FIRE_DAMPR_EN_ADDR | 802
FIRE_DAMPR_ADDR_START | 501
FIRE_DAMPR_REG | 1
FIRE_DAMPR_STRING_ID_START | 67
FIRE_DAMPR_CLOSED_EN_REG | 0
FIRE_DAMPR_CLOSED_EN_ADDR | 824
STATES |  | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto | NotOpened*Opened*Auto
CLOSED STATES |  | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto | NotClosed*Closed*Auto
ROOM_PRESSURES_EN_ADDR | 830
ROOM_PRESSURES_EN_REG | 4
ROOM_PRESSURES_REG | 3
ROOM_PRESSURES_ADDR_START | 301
ROOM_PRESSURES_STRING_ID_START | 267
ROOM_PRESSURES_SCALE | 0.1
VAV_SWITCHES_EN_REG | 1
VAV_SWITCHES_EN_ADDR | 811
VAV_SWITCHES_REG | 1
VAV_SWITCHES_ADDR_START | 201
VAV_SWITCHES_STRING_ID_START | 287
VAV_SWITCHES_MAX_COUNT | 20
STATES |  | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
Object ID | Signal name | String ID | En Reg | En Addr | En TPConfigDW | En condition | En bit pos | Reg | Addr | Scale | Data Type | State Lan1 | State Lan2 | State Lan3 | State Lan4 | State Lan5 | State Lan6 | State Lan7 | State Lan8 | State Lan9
#GROUP# DIGITAL
0x2204 'Unit1\DigitalInp.OADmpOpnd' | Outs air dampr fdbk | 1 | 0 | 822 | x | x | x | 1 | 171 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2204 'Unit1\DigitalInp.ExhADmpOpnd' | Exh air dampr fdbk | 2 | 0 | 823 | x | x | x | 1 | 172 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2204 'Unit1\DigitalInp.AirFlowSwitch' | Air flow switch | 3 | 0 | 825 | x | x | x | 1 | 173 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2204 'Unit1\DigitalInp.ExternalStart' | Remote start | 4 | 0 | 803 | x | x | x | 1 | 174 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2204 'Unit1\DigitalInp.ChovrTstatClg' | Chovr thermostat | 5 | 4 | 823 | x | == 1 | x | 1 | 175 | x | x | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto | Heating*Cooling*Auto
0x2204 'Unit1\DigitalInp.VRFStatus' | VRF status | 6 | 1 | 806 | x | x | x | 1 | 176 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2204 'Unit1\DigitalInp.VRFDefrost' | VRF defrost | 7 | 1 | 807 | x | x | x | 1 | 177 | x | x | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto
0x2204 'Unit1\DigitalInp.VRF2Status' | VRF2 status | 8 | 1 | 808 | x | x | x | 1 | 178 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2204 'Unit1\DigitalInp.VRF2Defrost' | VRF2 defrost | 9 | 1 | 809 | x | x | x | 1 | 179 | x | x | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto | Normal*Defrost*Auto
0x2205 'Unit1\DigitalInp.VRFMode' | VRF Mode | 10 | 1 | 831 | x | x | x | 3 | 34 | x | x | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating
0x2205 'Unit1\DigitalInp.VRF2Mode' | VRF2 Mode | 11 | 1 | 832 | x | x | x | 3 | 35 | x | x | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating | Auto*Fan*Defrost*Cooling*Heating
#GROUP# ANALOG
0x2300 'Unit1\DigitalInp.FDampInputs.FDampAlmTiDly' | Fire dmpr open time | 12 | 4 | 802 | x | > 0 | x | 3 | 33 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.ExtTempSpv' | External setpoint | 13 | 1 | 833 | x | x | x | 3 | 41 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TOutdoor' | Outdoor temperature | 14 | 1 | 834 | x | x | x | 3 | 42 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TOutsideAir' | Outside air temp | 15 | 1 | 835 | x | x | x | 3 | 43 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TSupplyAir' | Supply air temp | 16 | 1 | 836 | x | x | x | 3 | 44 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TExtractAir' | Extract air temp | 17 | 1 | 837 | x | x | x | 3 | 45 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TRoom' | Room temperature | 18 | 1 | 838 | x | x | x | 3 | 46 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TRoomUnit' | Room unit temp | 19 | 1 | 839 | x | x | x | 3 | 47 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TExhaustAir' | Exhaust air tmp | 20 | 1 | 840 | x | x | x | 3 | 48 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TBfClr' | Tmp before cooler | 21 | 1 | 841 | x | x | x | 3 | 49 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TAfClr' | Tmp after cooler | 22 | 1 | 842 | x | x | x | 3 | 50 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.B11-Temp' | B11-Temperature | 23 | 1 | 843 | x | x | x | 3 | 51 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.B12-Temp' | B12-Temperature | 24 | 1 | 844 | x | x | x | 3 | 52 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.B13-Temp' | B13-Temperature | 25 | 1 | 845 | x | x | x | 3 | 53 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.B14-Temp' | B14-Temperature | 26 | 1 | 846 | x | x | x | 3 | 54 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TAux1' | Auxiliary tmp 1 | 27 | 1 | 847 | x | x | x | 3 | 55 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TAux2' | Auxiliary tmp 2 | 28 | 1 | 848 | x | x | x | 3 | 56 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TAux3' | Auxiliary tmp 3 | 29 | 1 | 849 | x | x | x | 3 | 57 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.TAux4' | Auxiliary tmp 4 | 30 | 1 | 850 | x | x | x | 3 | 58 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.HuRelSplyAir' | Sply air hum rel | 31 | 1 | 851 | x | x | x | 3 | 59 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.HuRelExtAir' | Extract air hum rel | 32 | 1 | 852 | x | x | x | 3 | 60 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.HuRelRoom' | Room humidity rel | 33 | 1 | 853 | x | x | x | 3 | 61 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.HuRelOutAir' | Outs air hum rel | 34 | 1 | 854 | x | x | x | 3 | 62 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\AnalogInp.EnthSplyAir' | Supply air enthalpy | 35 | 1 | 851 | x | x | x | 3 | 63 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\AnalogInp.HumAbsSplyAir' | Supply air hum abs | 36 | 1 | 851 | x | x | x | 3 | 64 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\AnalogInp.EnthExtAir' | Extract air enthalpy | 37 | 1 | 852 | x | x | x | 3 | 65 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\AnalogInp.HumAbsExtAir' | Extract air hum abs | 38 | 1 | 852 | x | x | x | 3 | 66 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\AnalogInp.EnthOutAir' | Outs air enthalpy | 39 | 1 | 853 | x | x | x | 3 | 67 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\AnalogInp.HumAbsOutAir' | Outs air hum abs | 40 | 1 | 853 | x | x | x | 3 | 68 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AirQuality' | Air quality | 41 | 1 | 855 | x | x | x | 3 | 69 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AirQuality2' | Air quality 2 | 42 | 1 | 856 | x | x | x | 3 | 70 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AirQuality3' | Air quality 3 | 43 | 1 | 857 | x | x | x | 3 | 71 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AirQuality4' | Air quality 4 | 44 | 1 | 858 | x | x | x | 3 | 72 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.DiffPSenSuFan' | Pressure supply fan | 45 | 1 | 859 | x | x | x | 3 | 73 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.DiffPSenExFan' | Pressure extract fan | 46 | 1 | 860 | x | x | x | 3 | 74 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.DiffPSenSuAir' | Supply air pressure | 47 | 1 | 861 | x | x | x | 3 | 75 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.DiffPSenExAir' | Extract air pressure | 48 | 1 | 862 | x | x | x | 3 | 76 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.FreshAirFilter' | Fresh air filter | 49 | 1 | 863 | x | x | x | 3 | 77 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.ExtAirFilter' | Extract filter | 50 | 1 | 864 | x | x | x | 3 | 78 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.SplyAirFilter' | Supply filter | 51 | 1 | 865 | x | x | x | 3 | 79 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.ExhAirFilter' | Exhaust filter | 52 | 1 | 866 | x | x | x | 3 | 80 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AuxSplyFilter' | 2 Aux supply filter | 53 | 1 | 867 | x | x | x | 3 | 81 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AuxSplyFilter2' | 3 Aux supply filter | 54 | 1 | 868 | x | x | x | 3 | 82 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AuxExtFilter' | 2 Aux extract filter | 55 | 1 | 869 | x | x | x | 3 | 83 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2203 'Unit1\AnalogInp.AuxExtFilter2' | 3 Aux extract filter | 56 | 1 | 870 | x | x | x | 3 | 84 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\FanControl.FlowSplyAir' | Supply air flow | 57 | 1 | 871 | x | x | x | 3 | 85 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\FanControl.FlowExtAir' | Extract air flow | 58 | 1 | 872 | x | x | x | 3 | 87 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\FanControl.DuctPressSply' | Supply air pressure | 59 | 1 | 873 | x | x | x | 3 | 89 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\FanControl.DuctPressExt' | Extract air pressure | 60 | 1 | 874 | x | x | x | 3 | 90 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\aoKNX.RcvDDC1Value2' | Outdoor temperature 2 | 61 | 1 | 875 | x | x | x | 3 | 91 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x230A 'Unit1\aoKNX.RcvDDC2Value2' | Outdoor temperature 1 | 62 | 1 | 876 | x | x | x | 3 | 92 | 0.1 | 1 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\ModbusMS.PowerSplyFan' | Supply fan power | 63 | x | x | 2 | x | 23 | 3 | 131 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\FanControl.SFPValueSplyFan' | SFP supply fan | 64 | x | x | 2 | x | 23 | 3 | 132 | 0.001 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\ModbusMS.PowerExtrFan' | Ext fan power | 65 | x | x | 2 | x | 24 | 3 | 146 | 1.0 | 0 | x | x | x | x | x | x | x | x | x
0x2200 'Unit1\FanControl.SFPValueExtFan' | SFP extract fan | 66 | x | x | 2 | x | 24 | 3 | 147 | 0.001 | 0 | x | x | x | x | x | x | x | x | x