## Sheet1
Version: 1
Object ID | Signal name | String ID | En Reg | En Addr | En TPConfigDW | En condition | en bit pos | reg | addr | disabled | State L1 | State L2 | State L3 | State L4 | State L5 | State L6 | State L7 | State L8 | State L9
#GROUP# MAIN DIGITAL
0x2202 'Unit1\PlantPoint' | Operating mode | 1 | 1 | 701 | x | x | x | 4 | 21 | FALSE | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling
0x2202 'Unit1\PlantPoint' | Act Operating mode | 2 | 1 | 701 | x | x | x | 3 | 121 | TRUE | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling | Auto*Off*BuildProt*Economy*Comfort*FreeCooling
0x2302 'Unit1\TempControl.TmpRegSel' | Tmp control mode | 3 | 0 | 843 | x | x | x | 4 | 22 | FALSE | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT | SplyT*ExtT*RoomT
0x2302 'Unit1\aoHumitityControl.HumRegSel' | Hum control mode | 4 | 1 | 850 | x | x | x | 4 | 24 | FALSE | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH | SplyH*ExtH*RmH
0x2202 'Unit1\aoHumitityControl.SPSELHumidity' | Hum stpt selection | 5 | 1 | 850 | x | x | x | 4 | 25 | TRUE | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz | Hum/Dehum*+/- 1/2Dz*Hum+Dz*Dehum-Dz
0x2302 'Unit1\FanControl.ExtFan2OpMode' | 2 Extract fan mode | 6 | 4 | 811 | x | > 0 | x | 4 | 29 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan3OpMode' | 3 Extract fan mode | 7 | 4 | 812 | x | > 1 | x | 4 | 30 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan4OpMode' | 4 Extract fan mode | 8 | 4 | 813 | x | > 2 | x | 4 | 31 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan5OpMode' | 5 Extract fan mode | 9 | 4 | 814 | x | > 3 | x | 4 | 32 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan6OpMode' | 6 Extract fan mode | 10 | 4 | 815 | x | > 4 | x | 4 | 33 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan7OpMode' | 7 Extract fan mode | 11 | 4 | 816 | x | > 5 | x | 4 | 34 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan8OpMode' | 8 Extract fan mode | 12 | 4 | 817 | x | > 6 | x | 4 | 35 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.ExtFan9OpMode' | 9 Extract fan mode | 13 | 4 | 818 | x | > 7 | x | 4 | 36 | FALSE | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On | Auto*Off*On
0x2302 'Unit1\FanControl.DmpDlyOffFireEn' | Damper dly off - fire | 14 | x | x | 0 |  | 4 | 0 | 35 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 'Unit1\FanControl.FireMode' | Fire mode | 15 | x | x | 0 |  | 6 | 4 | 26 | FALSE | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn | Null*SFEFOff*EFOff*SFOff*SFEFOn
#GROUP# ADVANCED DIGITAL
0x2302 'InOutp\InOutp.SFDiffPSenScale' | Scale pressure supply fan | 1 | x | x | 2 | x | 14 | 4 | 162 | FALSE | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa
0x2302 'InOutp\InOutp.EFDiffPSenScale' | Scale pressure extract fan | 2 | x | x | 2 | x | 15 | 4 | 163 | FALSE | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa | Other*1000Pa*2000Pa*3000Pa*5000Pa
0x2302 'Unit1\ModbusMS.MB_FanErrEn' | Modbus fan error | 3 | x | x | 0 | x | 5 | 0 | 36 | FALSE | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On
0x2302 'Unit1\TempControl.CasCtrEn' | Cascade controller | 4 | x | x | 0 | x | 1 | 0 | 31 | FALSE | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On
0x2302 'Unit1\TempControl.DehumSpvMinTEn' | Dehum tmp min stpt | 5 | x | x | 0 | x | 3 | 0 | 34 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 'Unit1\TempControl.TOutThEn' | Disable by outs tmp | 6 | 0 | 843 | x | x | x | 4 | 23 | FALSE | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On
0x2302 0x00003AB1 | El heating | 7 | x | x | x | x | x | 4 | 822 | FALSE | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St3 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St4 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St5 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St6 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St7 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St8 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St9 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St10 | NoElHtr*RegOutput*Reg+St1*Reg+St2*Reg+St3*St1*St2*St11
0x2302 'Unit1\FanControl.AirQRegSel' | Air quality control | 8 | 4 | 805 |  | < 2 | x | 4 | 27 | FALSE | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp | Fan*MixDmp*Fan+MixDmp
0x2302 'Unit1\FanControl.AirQAveMinMax' | Air quality mix | 9 | 4 | 804 |  | > 1 | x | 4 | 28 | FALSE | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max | Avg*Min*Max
0x2302 'Alarms\Alarms.ComAlarmPol' | Common alarm polarity | 10 | 0 | 802 | x | x | x | 0 | 21 | FALSE | Norm*Rev | Norm*Rev | Norm*Rev | Norm*Rev | Norm*Rev | Norm*Rev | Norm*Rev | Norm*Rev | Norm*Rev
0x2302 0x0000DD29 | Enable all obj. | 11 | x | x | x | x | x | 0 | 801 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000371C | Auto configuration IOs | 12 | x | x | x | x | x | 0 | 805 | FALSE | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On | Off*On
0x2302 0x0000236A | Room unit | 13 | x | x | x | x | x | 0 | 873 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00006C01 | Tmp stpt selection | 14 | x | x | x | x | x | 4 | 819 | FALSE | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo | SPV+DB*SPVH+SPVC*SPVHtgCurvo
0x2203 'Unit1\AnalogInp.HuRelRoom' | Humidity | 15 | x | x | x | x | x | 0 | 912 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00007DD0 | Dehumidification | 16 | x | x | x | x | x | 0 | 913 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00009B65 | Common alarm | 17 | x | x | x | x | x | 0 | 802 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
#GROUP# ADVANCED INPUTS
0x2302 0x00008D0B | Outs air dampr fdbk | 1 | x | x | x | x | x | 0 | 822 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00006BC8 | Exh air dampr fdbk | 2 | x | x | x | x | x | 0 | 823 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000558F | Extract air pressure | 3 | x | x | x | x | x | 0 | 831 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00008D92 | Supply air pressure | 4 | x | x | x | x | x | 0 | 830 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00001E6B | Supply air pressure switch | 5 | x | x | x | x | x | 0 | 821 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000322C | Extract air pressure switch | 6 | x | x | x | x | x | 4 | 801 | FALSE | 0*1*2*3*4*5*6*7*8*9 | 0*1*2*3*4*5*6*7*8*10 | 0*1*2*3*4*5*6*7*8*11 | 0*1*2*3*4*5*6*7*8*12 | 0*1*2*3*4*5*6*7*8*13 | 0*1*2*3*4*5*6*7*8*14 | 0*1*2*3*4*5*6*7*8*15 | 0*1*2*3*4*5*6*7*8*16 | 0*1*2*3*4*5*6*7*8*17
0x2302 0x0000ADAC | Air flow switch | 7 | x | x | x | x | x | 0 | 825 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00007009 | Filter alarm | 8 | x | x | x | x | x | 0 | 804 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00001F3D | Fresh air filter | 9 | x | x | x | x | x | 0 | 811 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000E4D0 | Supply filter | 10 | x | x | x | x | x | 0 | 812 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000081DE | Extract filter | 11 | x | x | x | x | x | 0 | 813 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000E4CE | Exhaust filter | 12 | x | x | x | x | x | 0 | 814 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000025E3 | 2 Aux supply filter | 13 | x | x | x | x | x | 0 | 815 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00009D2B | 3 Aux supply filter | 14 | x | x | x | x | x | 0 | 816 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000D725 | 2 Aux extract filter | 15 | x | x | x | x | x | 0 | 817 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00009476 | 3 Aux extract filter | 16 | x | x | x | x | x | 0 | 818 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000845F | Remote start | 17 | x | x | x | x | x | 0 | 803 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000938D | Air quality | 18 | x | x | x | x | x | 4 | 804 | FALSE | 0*1*2*3*4 | 0*1*2*3*5 | 0*1*2*3*6 | 0*1*2*3*7 | 0*1*2*3*8 | 0*1*2*3*9 | 0*1*2*3*10 | 0*1*2*3*11 | 0*1*2*3*12
0x2302 0x00003938 | Outdoor temperature | 19 | x | x | x | x | x | 0 | 847 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000080F9 | Outside air temp | 20 | x | x | x | x | x | 0 | 841 | FALSE | None*Yes | None*Yes | None*Yes | None*Yes | None*Yes | None*Yes | None*Yes | None*Yes | None*Yes
0x2302 0x00009C60 | Supply air temp | 21 | x | x | x | x | x | 0 | 843 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000B835 | Extract air temp | 22 | x | x | x | x | x | 0 | 842 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000ABE4 | Room tmp sensor | 23 | x | x | x | x | x | 0 | 846 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000D78F | Tmp before cooler | 24 | x | x | x | x | x | 0 | 844 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00000F0D | Tmp after cooler | 25 | x | x | x | x | x | 0 | 845 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00008CD4 | B11-Temperature | 26 | x | x | x | x | x | 0 | 848 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000D584 | B12-Temperature | 27 | x | x | x | x | x | 0 | 849 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000AF39 | Aux tmp sensor | 28 | x | x | x | x | x | 4 | 803 | FALSE | 0*1*2*3*4 | 0*1*2*3*5 | 0*1*2*3*6 | 0*1*2*3*7 | 0*1*2*3*8 | 0*1*2*3*9 | 0*1*2*3*10 | 0*1*2*3*11 | 0*1*2*3*12
0x2302 0x000001CC | Humidifier | 29 | x | x | x | x | x | 0 | 911 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000F9BC | Outs air hum rel | 30 | x | x | x | x | x | 0 | 861 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000082CA | Extract air hum rel | 31 | x | x | x | x | x | 0 | 862 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000C4B4 | Room humidity rel | 32 | x | x | x | x | x | 0 | 863 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000B9D0 | Cooling pump | 33 | x | x | x | x | x | 0 | 893 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00004517 | Compressor | 34 | x | x | x | x | x | 0 | 894 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00000ECF | Fire damper closed | 35 | x | x | x | x | x | 0 | 824 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00004AB6 | External setpoint | 36 | x | x | x | x | x | 0 | 885 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
#GROUP# ADVANCED FAN
0x2302 0x00003D9C | Fan control mode | 1 | x | x | x | x | x | 4 | 805 | FALSE | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct | ppmVol*ppmPress*Volume*Pressure*FixedSpeed*Direct
0x2302 0x0000236A | Room unit | 2 | x | x | x | x | x | 0 | 873 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000E408 | Duct pres stpt by rm unit | 3 | x | x | x | x | x | 0 | 874 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00006048 | Following system | 4 | x | x | x | x | x | 0 | 871 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000F474 | Fans nr | 5 | x | x | x | x | x | 4 | 806 | FALSE | 0*1*2 | 0*1*3 | 0*1*4 | 0*1*5 | 0*1*6 | 0*1*7 | 0*1*8 | 0*1*9 | 0*1*10
0x2302 0x000064CF | Outputs fans | 6 | x | x | x | x | x | 4 | 807 | FALSE | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt | No*SFStt*EFStt*SFStt+EFStt
0x2302 0x00001010 | Fan state | 7 | x | x | x | x | x | 0 | 872 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00009AB1 | Dampers | 8 | x | x | x | x | x | 4 | 808 | FALSE | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh | No*Sply*Exh*Sply+Exh
0x2302 0x0000952F | Supply fan | 9 | x | x | x | x | x | 4 | 809 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000F838 | Extract fan | 10 | x | x | x | x | x | 4 | 810 | FALSE | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct | Disable*Default*Fix Speed*Direct
0x2302 0x00005CFB | 2 Extract fan | 11 | x | x | x | x | x | 4 | 811 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x00006BCB | 3 Extract fan | 12 | x | x | x | x | x | 4 | 812 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x0000EE5B | 4 Extract fan | 13 | x | x | x | x | x | 4 | 813 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x0000D96B | 5 Extract fan | 14 | x | x | x | x | x | 4 | 814 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x0000803B | 6 Extract fan | 15 | x | x | x | x | x | 4 | 815 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x0000B70B | 7 Extract fan | 16 | x | x | x | x | x | 4 | 816 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x00009B3A | 8 Extract fan | 17 | x | x | x | x | x | 4 | 817 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x0000AC0A | 9 Extract fan | 18 | x | x | x | x | x | 4 | 818 | FALSE | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct | Disable*Fix Speed*Direct
0x2302 0x00000A27 | Supply VAVs | 19 | x | x | x | x | x | 0 | 875 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00000ECF | Fire damper closed | 20 | x | x | x | x | x | 0 | 824 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
#GROUP# ADVANCED TEMP
0x2302 0x00006C01 | Tmp stpt selection | 1 | x | x | x | x | x | 4 | 819 | FALSE | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve | SPV+DB*SPVH+SPVC*SPVHtgCurve
0x2302 0x0000C8DA | Chovr type select | 2 | x | x | x | x | x | 4 | 823 | FALSE | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens | NO*ChovrTstat*ChovrSens*CoilSens
0x2302 0x00002CF9 | Hrec frost protect | 3 | x | x | x | x | x | 0 | 886 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00007924 | Pre heating | 4 | x | x | x | x | x | 0 | 882 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000C2F3 | Free cooling | 5 | x | x | x | x | x | 0 | 884 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000048AB | Mixing damper | 6 | x | x | x | x | x | 0 | 887 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000029A3 | Heat recovery | 7 | x | x | x | x | x | 4 | 820 | FALSE | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC | NoHREC*PlateHREC*Rothoterm*Polyblock*GlycolHREC
0x2302 0x0000C73F | Heating | 8 | x | x | x | x | x | 0 | 888 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000077B6 | Cooling | 9 | x | x | x | x | x | 0 | 892 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 'Unit1\TempControl.ElHeaterInSeq' | El heating | 10 | 4 | 822 |  | > 0 | x | 0 | 32 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000061F0 | El heater on ext | 11 | x | x | x | x | x | 0 | 889 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00007400 | 2 El heating | 12 | x | x | x | x | x | 0 | 890 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000034FF | 3 El heating | 13 | x | x | x | x | x | 0 | 891 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x000010EB | VRF type sel | 14 | x | x | x | x | x | 4 | 821 | FALSE | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason | NoVRF*Mitsubishi1*Mitsubishi2*Mitsubishi3*Daikin*SamsungAlfa*RTD10_FDP3*Panason
0x2302 0x000049F1 | VRF in sequence | 15 | x | x | x | x | x | 0 | 899 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000C130 | VRF reg by dT | 16 | x | x | x | x | x | 0 | 898 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000CD70 | VRF vent mode | 17 | x | x | x | x | x | 0 | 897 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000C67E | VRF auto mode | 18 | x | x | x | x | x | 0 | 896 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00005182 | VRF 2 | 19 | x | x | x | x | x | 0 | 895 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x00003817 | Siphon heater | 20 | x | x | x | x | x | 0 | 881 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
0x2302 0x0000A45A | Piping heater | 21 | x | x | x | x | x | 0 | 883 | FALSE | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES | NO*YES
Note on A43: Author: Ispitiati točku