## Sheet1
Version: 1
Var name | Value
VAV_NUMBER_REG | 4
VAV_NUMBER_ADDR | 830
VAV_STRING_ID_START | 378
VAV_ADDR_START | 301
VAV_REG | 3
VAV_DATA_TYPE | 1
VAV_SCALE | 0.1
VAV_SPLY_REG_EN_REG | 1
VAV_SPLY_REG_EN_ADDR_START | 811
Object ID | Signal name | String ID | En Reg | En Addr | En TPConfigDW | En condition | En bit pos | Reg | Addr | Scale | Data Type | State Lan1 | State Lan2 | State Lan3 | State Lan4 | State Lan5 | State Lan6 | State Lan7 | State Lan8 | State Lan9
#GROUP# DIGITAL
0x2207 'Unit1\FanControl.OutAirDmpOn' | Outs air damper cmd | 307 | 1 | 877 | x | x | x | 1 | 221 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExhAirDmpOn' | Exhaust air damper cmd | 308 | 1 | 878 | x | x | x | 1 | 222 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.SplyFanStart' | Supply fan cmd | 309 | 1 | 879 | x | x | x | 1 | 223 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFanStart' | Extract fan cmd | 310 | 1 | 880 | x | x | x | 1 | 224 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan2Start' | 2 Extract fan cmd | 311 | 1 | 881 | x | x | x | 1 | 225 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan3Start' | 3 Extract fan cmd | 312 | 1 | 882 | x | x | x | 1 | 226 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan4Start' | 4 Extract fan cmd | 313 | 1 | 883 | x | x | x | 1 | 227 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan5Start' | 5 Extract fan cmd | 314 | 1 | 884 | x | x | x | 1 | 228 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan6Start' | 6 Extract fan cmd | 315 | 1 | 885 | x | x | x | 1 | 229 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan7Start' | 7 Extract fan cmd | 316 | 1 | 886 | x | x | x | 1 | 230 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan8Start' | 8 Extract fan cmd | 317 | 1 | 887 | x | x | x | 1 | 231 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.ExtFan9Start' | 9 Extract fan cmd | 318 | 1 | 888 | x | x | x | 1 | 232 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.FanRunStatus' | Fan state | 319 | 1 | 889 | x | x | x | 1 | 233 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\FanControl.GasValve' | Gas valve | 320 | 1 | 890 | x | x | x | 1 | 234 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\TempControl.HrcStart' | Hrec command | 321 | 1 | 891 | x | x | x | 1 | 235 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.HtgPmpStart' | Htg pump cmd | 322 | 1 | 892 | x | x | x | 1 | 236 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.ClgPmpStart' | Cooling pump cmd | 323 | 1 | 893 | x | x | x | 1 | 237 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.CompressorStart' | Compressor command | 324 | 1 | 894 | x | x | x | 1 | 238 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.HtgClgPmpStart' | Htg/Clg pump command | 325 | 1 | 895 | x | x | x | 1 | 239 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.ElHeater.ElHeaterStart' | El heating cmd | 326 | 1 | 896 | x | x | x | 1 | 240 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.ElHeater.ElHeaterSt1' | El heating stage 1 | 327 | 1 | 897 | x | x | x | 1 | 241 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.ElHeater.ElHeaterSt2' | El heating stage 2 | 328 | 1 | 898 | x | x | x | 1 | 242 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.ElHeater.ElHeaterSt3' | El heating stage 3 | 329 | 1 | 899 | x | x | x | 1 | 243 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.CoolingSignal' | Su/Wi mode cooling | 330 | 1 | 900 | x | x | x | 1 | 244 | x | x | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto | ----*Cooling*Auto
0x2207 'Unit1\TempControl.HeatingSignal' | Su/Wi mode heating | 331 | 1 | 901 | x | x | x | 1 | 245 | x | x | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto | ----*Heating*Auto
0x2207 'Unit1\TempControl.SifonHtrOn' | Siphon heater | 332 | 1 | 902 | x | x | x | 1 | 246 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\TempControl.PipingHtrStart' | Piping heater | 333 | 1 | 903 | x | x | x | 1 | 247 | x | x | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL | Off*On*NULL
0x2207 'Unit1\TempControl.AuxElHtrStart' | 1 El heating cmd | 334 | 1 | 904 | x | x | x | 1 | 248 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.AuxElHtr2Start' | 2 El heating cmd | 335 | 1 | 905 | x | x | x | 1 | 249 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\aoHumitityControl.HumidifierStart' | Humidifier cmd | 336 | 1 | 906 | x | x | x | 1 | 250 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Alarms\Alarms.CommonAlm' | Common alarm | 337 | 1 | 907 | x | x | x | 1 | 251 | x | x | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto | OK*Alarm*Auto
0x2208 'Unit1\TempControl.AuxElHtg1.CmdSt.St' | 1 Electrical heating | 350 | 1 | 936 | x | x | x | 3 | 177 | x | x | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3
0x2208 'Unit1\TempControl.AuxElHtg2.CmdSt.St' | El heating cmd | 351 | 1 | 938 | x | x | x | 3 | 179 | x | x | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3 | Auto*Off*St1*St2*St3
0x2207 'Unit1\TempControl.VRF.VRFStart' | VRF command | 338 | 1 | 908 | x | x | x | 1 | 301 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.VRF.VRFChovr' | VRF Htg/Clg command | 339 | 1 | 909 | x | x | x | 1 | 302 | x | x | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto
0x2207 'Unit1\TempControl.VRF.VRFChovrClg' | VRF Su/Wi command | 340 | 1 | 910 | x | x | x | 1 | 303 | x | x | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto
0x2207 'Unit1\TempControl.VRF.VRFChovrHtg' | VRF Su/Wi command | 341 | 1 | 911 | x | x | x | 1 | 304 | x | x | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto
0x2207 'Unit1\TempControl.VRF.VRFFanMode' | VRF vent mode | 342 | 1 | 912 | x | x | x | 1 | 305 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.VRF.VRFThermalMode' | VRF thermal mode | 343 | 1 | 913 | x | x | x | 1 | 306 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.VRF.VRF2Start' | VRF2 command | 344 | 1 | 914 | x | x | x | 1 | 307 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.VRF.VRF2Chovr' | VRF2 Htg/Clg command | 345 | 1 | 915 | x | x | x | 1 | 308 | x | x | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto | Cooling*Heating*Auto
0x2207 'Unit1\TempControl.VRF.VRF2ChovrClg' | VRF2 Su/Wi command | 346 | 1 | 916 | x | x | x | 1 | 309 | x | x | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto | ----*COOLING*Auto
0x2207 'Unit1\TempControl.VRF.VRF2ChovrHtg' | VRF2 Su/Wi command | 347 | 1 | 917 | x | x | x | 1 | 310 | x | x | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto | ----*HEATING*Auto
0x2207 'Unit1\TempControl.VRF.VRF2FanMode' | VRF2 vent mode | 348 | 1 | 918 | x | x | x | 1 | 311 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
0x2207 'Unit1\TempControl.VRF.VRF2ThermalMode' | VRF2 thermal mode | 349 | 1 | 919 | x | x | x | 1 | 312 | x | x | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto | Off*On*Auto
#GROUP# ANALOG
0x2206 'Unit1\FanControl.SplyFanCtrl.Var.Pos' | Sply fan outp sign | 352 | 1 | 920 | x | x | x | 3 | 161 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFanCtrl.Var.Pos' | Extr fan outp signal | 353 | 1 | 921 | x | x | x | 3 | 162 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan2Ctrl.Var.Pos' | 2 Extr fan outp signal | 354 | 1 | 922 | x | x | x | 3 | 163 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan3Ctrl.Var.Pos' | 3 Extr fan outp signal | 355 | 1 | 923 | x | x | x | 3 | 164 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan4Ctrl.Var.Pos' | 4 Extr fan outp signal | 356 | 1 | 924 | x | x | x | 3 | 165 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan5Ctrl.Var.Pos' | 5 Extr fan outp signal | 357 | 1 | 925 | x | x | x | 3 | 166 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan6Ctrl.Var.Pos' | 6 Extr fan outp signal | 358 | 1 | 926 | x | x | x | 3 | 167 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan7Ctrl.Var.Pos' | 7 Extr fan outp signal | 359 | 1 | 927 | x | x | x | 3 | 168 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan8Ctrl.Var.Pos' | 8 Extr fan outp signal | 360 | 1 | 928 | x | x | x | 3 | 169 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\FanControl.ExtFan9Ctrl.Var.Pos' | 9 Extr fan outp signal | 361 | 1 | 929 | x | x | x | 3 | 170 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.MixDmpReg' | Mixing dampers outp signal | 362 | 1 | 930 | x | x | x | 3 | 171 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.HrcReg' | Hrec outp signal | 363 | 1 | 931 | x | x | x | 3 | 172 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.HtgVlvReg' | Heating outp signal | 364 | 1 | 932 | x | x | x | 3 | 173 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.ClgVlvReg' | Cooling outp signal | 365 | 1 | 933 | x | x | x | 3 | 174 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.HtgClgVlvReg' | Htg/Clg outp signal | 366 | 1 | 934 | x | x | x | 3 | 175 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.ElHeater.ElHeaterReg' | El heating outp signal | 367 | 1 | 935 | x | x | x | 3 | 176 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.AuxElHtg1.Pos' | El heating | 368 | 1 | 937 | x | x | x | 3 | 178 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.AuxElHtg2.Pos' | 2 Electrical heating | 369 | 1 | 939 | x | x | x | 3 | 180 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\aoHumitityControl.HumidifierReg' | Hum outp signal | 370 | 1 | 940 | x | x | x | 3 | 181 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\aoHumitityControl.DeHumidifierReg' | Dehum outp signal | 371 | 1 | 941 | x | x | x | 3 | 182 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.VRF.VRFReg' | VRF outp signal | 372 | 1 | 942 | x | x | x | 3 | 201 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.VRF.VRFStartAO' | VRF command AO | 373 | 1 | 943 | x | x | x | 3 | 202 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.VRF.VRFChovrAO' | VRF Htg/Clg AO | 374 | 1 | 944 | x | x | x | 3 | 203 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.VRF.VRF2Reg' | VRF2 outp signal | 375 | 1 | 945 | x | x | x | 3 | 204 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.VRF.VRF2StartAO' | VRF2 command AO | 376 | 1 | 946 | x | x | x | 3 | 205 | 0.1 | 0 | x | x | x | x | x | x | x | x | x
0x2206 'Unit1\TempControl.VRF.VRF2ChovrAO' | VRF2 Htg/Clg AO | 377 | 1 | 947 | x | x | x | 3 | 206 | 0.1 | 0 | x | x | x | x | x | x | x | x | x